## 工作表1
暫存器DEC | 暫存器HEX | NAME | 資料型態 | Access | Offset | 倍率 | ByteCount | 單位 | 備註 | Madeili 說明 | Madeili 說明 | Madeili 頁面說明 | MCU data Source | MCU data Source
0 | 0000 | Voltage | unsigned | R | 0 | 1 | 2 | mV |  | TI Data+MCU Data | 總電壓 (16串電壓總合) | Voltage | bms.voltage
1 | 0001 | Current | signed | R | 0 | 1 | 2 | 10mA |  | TI Data | 電流 (正: 充電。負:放電) | Current | bms.current
2 | 0002 | RemainingCapacity | unsigned | R | 0 | 1 | 2 | 10mAH |  | TI Data | 剩餘容量 |  | bms.remainingcapacity
3 | 0003 | FullChargeCapacity | unsigned | R | 0 | 1 | 2 | 10mAH |  | TI Data | 全充容量 |  | bms.fullchargecapacity
4 | 0004 | CycleCount | unsigned | R | 0 | 1 | 2 |  |  | TI Data | 充放循環次數 | Cycle Count | device.cyclecount
5 | 0005 | StateOfHealth | unsigned | R | 0 | 1 | 2 | % |  | TI Data | 電池健康度 | State Of Health | device.stateofjealth
6 | 0006 | RelativeStateOfCharge | unsigned | R | 0 | 1 | 2 | % |  | TI Data | 電量百分比 | Battery Capacity | device.relativestateofcharge
7 | 0007 | BMSOperationStaus | unsigned | R | 0 | 1 | 2 |  | b4:CB b3. HCFET b2:PDSG b1:DSG b0:CHG | TI Data TI+MCU Data (綠色部份合併TI) | b4:電池平衡功能 b3: MCU主動控制 FET b2:預放電功能 b1:放電控制端子 b0:充電控制端子 |  | bms.operationstatus | b4:bms.CB b2:device.operationstatusbits.PDSG b1:device.operationstatusbits.DSG b0:device.operationstatusbits.CHG
8 | 0008 | BMSSafetyStaus | unsigned | R | 0 | 1 | 2 |  | b11:UTD b10:UTC b9:OTD b8:OTC b7:ASCDL b6:ASCD b5:AOLDL b4:AOLD b3:OCD b2:OCC b1:COV b0:CUV | TI Data TI+MCU Data (綠色部份合併TI) | b11:低溫放電保護 b10:低溫充電保護 b9:高溫放電保護 b8:高溫充電保護 b7:短路栓鎖保護 b6:短路保護 b5:放電過流第二段栓鎖保護 b4:放電過流第二段保護 b3:放電過流保護 b2:充電過流保護 b1:單體電池過壓保護 b0:單體電池低壓保護 | b0~b11=0 => Normal b11:Undertemperature During Discharge b10:Undertemperature During Charge b9:Overtemperature During Discharge b8:Overtemperature During Charge b7:Short Circuit During Discharge Latch b6:Short Circuit During Discharge b5:Overload During Discharge Latch b4:Overload During Discharge b3:Overcurrent During Discharge b2:Overcurrent During Charge b1:Cell Overvoltage b0:Cell Undervoltage | bms.safetystatus | b11:bms.UTD b10:bms.UTC b9:bms.OTD b8:bms.OTC b7:device.safetystatusbits.ASCDL b6:device.safetystatusbits.ASCD b5:device.safetystatusbits.AOLDL b4:device.safetystatusbits.AOLD b3:device.safetystatusbits.OCD b2:device.safetystatusbits.OCC b1:bms.COV b0:bms.CUV
9 | 0009 | LED_ERROR0 | unsigned | R | 0 | 1 | 2 |  | b15:CUV b14:COV b13:OCC b12:OCD b11:AOLD b10:ASCD b9:OTC b8:OTD b7:UTC b6:UTD b3:CO_ON b2:Boot_ERROR b1:Shutdown_ERROR b0:CON_ERROR | TI Data TI+MCU Data (綠色部份合併TI) MCU Data 機殼面板會顯示的錯誤 ( 10進制顯示 ) | b15:單體電池低壓保護 b14:單體電池過壓保護 b13:充電過流保護 b12:放電過流保護 b11:放電過流第二段保護 b10:短路保護 b9:高溫充電保護 b8:高溫放電保護 b7:低溫充電保護 b6:低溫放電保護 b3:單體電池過壓第二段保護 b2:開機異常 b1:關機異常 b0:RS485通訊異常 | b15:Cell Undervoltage b14:Cell Overvoltage b13:Overcurrent During Charge b12:Overcurrent During Discharge b11:Overload During Discharge b10:Short Circuit During Discharge b9:Overtemperature During Charge b8:Overtemperature During Discharge b7:Undertemperature During Charge b6:Undertemperature During Discharge b5:reserve b4:reserve b3:2nd Cell Overvoltage b2:Boot Error b1:Communication Error |  | device.safetystatusbits.CUV ¦¦ bms.c16_uvp_sts
10 | 000A | PT_CTL0、1 | unsigned | R | 0 | 1 | 2 |  | b15:cmd_chg_fet_ctl b14:c16_ovp_sts b13:ntc1_chg_otp_sts b12:ntc2_chg_otp_sts b11:ntc3_chg_otp_sts b10:ntc1_chg_utp_sts b9:ntc2_chg_utp_sts b8:ntc3_chg_utp_sts b7:cmd_dsg_fet_ctl b6:c16_uvp_sts b5:ntc1_dsg_otp_sts b4:ntc2_dsg_otp_sts b3:ntc3_dsg_otp_sts b2:ntc1_dsg_utp_sts b1:ntc2_dsg_utp_sts b0:ntc3_dsg_utp_sts | MCU Data MCU控制CO/DO開關項目 | b15:工程指令CHG MOS控制 b14:CELL16 單體電池過壓保護 b13:NTC1高溫充電保護 b12:NTC2高溫充電保護 b11:NTC3高溫充電保護 b10:NTC1低溫充電保護 b9:NTC2低溫充電保護 b8:NTC3低溫充電保護 b7:工程指令DSG MOS控制 b6:CELL16 單體電池低壓保護 b5:NTC1高溫放電保護 b4:NTC2高溫放電保護 b3:NTC3高溫放電保護 b2:NTC1低溫放電保護 b1:NTC2低溫放電保護 b0:NTC3低溫放電保護
11 | 000B | PT_CTL2 | unsigned | R | 0 | 1 | 2 |  | b1:AOLDL_PT_dsg_fet_ctl b0:ASCDL_PT_dsg_fet_ctl | MCU Data 過流安規保護旗標 短路安規保護旗標 | 過流鎖住 -> 充電電流 > 2A 解除 短路鎖住 -> 充電電流 > 2A 解除
12 | 000C | reserve | unsigned | R | 0 | 1 | 2
13 | 000D | reserve | unsigned | R | 0 | 1 | 2
14 | 000E | reserve | unsigned | R | 0 | 1 | 2
15 | 000F | reserve | unsigned | R | 0 | 1 | 2
16 | 0010 | CellVoltage1 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串1 |  | device.cellvoltage[0]
17 | 0011 | CellVoltage2 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串2 |  | device.cellvoltage[1]
18 | 0012 | CellVoltage3 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串3 |  | device.cellvoltage[2]
19 | 0013 | CellVoltage4 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串4 |  | device.cellvoltage[3]
20 | 0014 | CellVoltage5 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串5 |  | device.cellvoltage[4]
21 | 0015 | CellVoltage6 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串6 |  | device.cellvoltage[5]
22 | 0016 | CellVoltage7 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串7 |  | device.cellvoltage[6]
23 | 0017 | CellVoltage8 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串8 |  | device.cellvoltage[7]
24 | 0018 | CellVoltage9 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串9 |  | device.cellvoltage[8]
25 | 0019 | CellVoltage10 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串10 |  | device.cellvoltage[9]
26 | 001A | CellVoltage11 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串11 |  | device.cellvoltage[10]
27 | 001B | CellVoltage12 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串12 |  | device.cellvoltage[11]
28 | 001C | CellVoltage13 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串13 |  | device.cellvoltage[12]
29 | 001D | CellVoltage14 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串14 |  | device.cellvoltage[13]
30 | 001E | CellVoltage15 | unsigned | R | 0 | 1 | 2 | mV |  | TI Data | 電池串15 |  | device.cellvoltage[14]
31 | 001F | CellVoltage16 | unsigned | R | 0 | 1 | 2 | mV |  | MCU Data | 電池串16 |  | device.cellvoltage[15]
32 | 0020 | Temperature1 | signed | R | -273 | 0.1 | 2 | ℃ |  | TI Data | 電池溫度1 | Battery Temperature1 | device.temp.TS1
33 | 0021 | Temperature2 | signed | R | -273 | 0.1 | 2 | ℃ |  | TI Data | 電池溫度2 | Battery Temperature2 | device.temp.TS2
34 | 0022 | Temperature3 | signed | R | -273 | 0.1 | 2 | ℃ |  | TI Data | 電池溫度3 | Battery Temperature3 | device.temp.TS3
35 | 0023 | Temperature4 | signed | R | -273 | 0.1 | 2 | ℃ |  | MCU Data | 電池溫度4 | Battery Temperature4 | bms.ntc1_temp
36 | 0024 | Temperature5 | signed | R | -273 | 0.1 | 2 | ℃ |  | MCU Data | FET溫度 | FET Temperature | bms.ntc2_temp
37 | 0025 | Temperature6 | signed | R | -273 | 0.1 | 2 | ℃ |  | MCU Data | 環境溫度 | Environment Temperature | bms.ntc3_temp
38 | 0026 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
39 | 0027 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
40 | 0028 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
41 | 0029 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
42 | 002A | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
43 | 002B | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
44 | 002C | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
45 | 002D | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
46 | 002E | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
47 | 002F | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
48 | 0030 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
49 | 0031 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
50 | 0032 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
51 | 0033 | Temperature |  |  |  |  | 2 |  |  | 保留, 目前沒使用
52 | 0034 | Temperature21 | signed | R | -273 | 0.1 | 2 | ℃ | 廠內使用 | TI Data | Gauge IC 內部溫度 |  | device.temp.Internal_Gauge_Temp
53 | 0035 | MaxError | unsigned | R | 0 | 1 | 2 | % | 廠內使用 | TI Data | RSOC最大誤差 This read-word function returns the expected margin of error, in %, in the state-of-charge calculation with a range of 1 to 100% |  | device.maxerror
54 | 0036 | PendingEDV | unsigned | R | 0 | 1 | 2 | mV | 廠內使用 | TI Data | EDV2 EDV1 預測電壓 This read-word function returns the predicted EDV2 until EDV2 is reached, then the predicted EDV1 until EDV1 is reached, and then the predicted EDV0. The format is Little Endian |  | device.pendingedv
55 | 0037 | ExtAveCellVoltage | unsigned | R | 0 | 1 | 2 | mV | 廠內使用 | TI Data | 16串電壓平均值 This read-word function returns the external average cell voltage measurement, if enabled, which can be used within the gas gauging algorithm for EDV2, EDV1, and EDV0 detection |  | device.extAvecellvoltage
56 | 0038 | BatteryStatus | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 電池狀態 This read-word function returns various battery status information |  | device.batterystatus
57 | 0039 | OperationStatus0 | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 運作狀態 This command returns the OperationStatus() flags on ManufacturerBlockAccess() or ManufacturerData(). |  | device.operationstatus[0]
58 | 003A | OperationStatus1 | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 運作狀態 This command returns the OperationStatus() flags on ManufacturerBlockAccess() or ManufacturerData(). |  | device.operationstatus[1]
59 | 003B | SafetyStatus0 | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 安全狀態 This command returns the SafetyStatus() flags on ManufacturerBlockAccess() or ManufacturerData() |  | device.safetystatus[0]
60 | 003C | SafetyStatus1 | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 安全狀態 This command returns the SafetyStatus() flags on ManufacturerBlockAccess() or ManufacturerData() |  | device.safetystatus[1]
61 | 003D | GaugingStatus | unsigned | R | 0 | 1 | 2 |  | 廠內使用 | TI Data | 容量計算狀態 This command returns the GaugingStatus() flags on ManufacturerBlockAccess() or ManufacturerData(). |  | device.gaugingstatus
62 | 003E | [8 empty] | 保留, 目前沒使用
63 | 003F | [8 empty] | 保留, 目前沒使用
64 | 0040 | Serial Number_1 | HexToChar | R |  |  | 8 | ASCII |  | TI Data 這三筆要合併後才看資料 | 原本是Device Name 拿來做 CTL Board 序號 |  | bms.device_name[0~7]
65 | 0041 | Serial Number_2 | HexToChar | R |  |  | 8 | ASCII |  |  |  |  | bms.device_name[8~15]
66 | 0042 | Serial Number_3 | HexToChar | R |  |  | 8 | ASCII |  |  |  |  | bms.device_name[16~23]
67 | 0043 | Manufacturer Name1 | HexToChar | R |  |  | 8 | ASCII |  | TI Data 這三筆要合併後才看資料 | 製造商名稱 |  | bms.manufacturer_name[0~7]
68 | 0044 | Manufacturer Name2 | HexToChar | R |  |  | 8 | ASCII |  |  |  |  | bms.manufacturer_name[8~15]
69 | 0045 | Manufacturer Name3 | HexToChar | R |  |  | 8 | ASCII |  |  |  |  | bms.manufacturer_name[16~23]
70 | 0046 | Manufacture Date | HexToChar | R |  |  | 8 | ASCII |  | TI Data | CTL Board 燒錄日期 |  | bms.manufacturer_date_year[0~3] bms.manufacturer_date_mon[0~1] bms.manufacturer_date_day[0~1]
71 | 0047 | Serial Number | HexToChar | R |  |  | 6 | ASCII |  | TI Data | CTL Board 燒錄日當天的序號 |  | bms.serial_number[0~5]
72 | 0048 | Device Chemistry1 | HexToChar | R |  |  | 4 | ASCII |  | TI Data | 電池種類 |  | bms.device_chemistry[0~3]
73 | 0049 | BMS_FW_VER 1 | HexToChar | R |  |  | 8 | ASCII |  | MCU Data 這二筆要合併後才看資料 | MCU韌體版本 |  | BMS_FW_VER[0~7]
74 | 004A | BMS_FW_VER 2 | HexToChar | R |  |  | 8 | ASCII |  |  |  |  | BMS_FW_VER[8~15]
75 | 004B | BMS_FW_DATE | HexToChar | R |  |  | 8 | ASCII |  | MCU Data | MCU 發版日期 |  | BMS_FW_DATE[0~7]
76 | 004C
77 | 004D
78 | 004E
79 | 004F
80 | 0050
81 | 0051
82 | 0052
83 | 0053
84 | 0054
85 | 0055
86 | 0056
87 | 0057
88 | 0058
89 | 0059
90 | 005A
91 | 005B
92 | 005C
93 | 005D
94 | 005E
95 | 005F
96 | 0060
97 | 0061
98 | 0062
99 | 0063
100 | 0064
101 | 0065
102 | 0066
103 | 0067
104 | 0068
105 | 0069
106 | 006A
107 | 006B
108 | 006C
109 | 006D
110 | 006E
111 | 006F
112 | 0070
113 | 0071
114 | 0072
115 | 0073
116 | 0074
117 | 0075
118 | 0076
119 | 0077
120 | 0078
121 | 0079
122 | 007A
123 | 007B
124 | 007C
125 | 007D
126 | 007E
127 | 007F
128 | 0080
129 | 0081
130 | 0082
131 | 0083
132 | 0084
133 | 0085
134 | 0086
135 | 0087
136 | 0088
137 | 0089
138 | 008A
139 | 008B
140 | 008C
141 | 008D
142 | 008E
143 | 008F
144 | 0090
145 | 0091
146 | 0092
147 | 0093
148 | 0094
149 | 0095
150 | 0096
151 | 0097
152 | 0098
153 | 0099
154 | 009A
155 | 009B
156 | 009C
157 | 009D
158 | 009E
159 | 009F
160 | 00A0
161 | 00A1
162 | 00A2
163 | 00A3
164 | 00A4
165 | 00A5
166 | 00A6
167 | 00A7
168 | 00A8
169 | 00A9
170 | 00AA
171 | 00AB
172 | 00AC
173 | 00AD
174 | 00AE
175 | 00AF
176 | 00B0
177 | 00B1
178 | 00B2
179 | 00B3
180 | 00B4
181 | 00B5
182 | 00B6
183 | 00B7
184 | 00B8
185 | 00B9
186 | 00BA
187 | 00BB
188 | 00BC
189 | 00BD
190 | 00BE
191 | 00BF
192 | 00C0
193 | 00C1
194 | 00C2
195 | 00C3
196 | 00C4
197 | 00C5
198 | 00C6
199 | 00C7
200 | 00C8
201 | 00C9
202 | 00CA
203 | 00CB
204 | 00CC
205 | 00CD
206 | 00CE
207 | 00CF
208 | 00D0
209 | 00D1
210 | 00D2
211 | 00D3
212 | 00D4
213 | 00D5
214 | 00D6
215 | 00D7
216 | 00D8
217 | 00D9
218 | 00DA
219 | 00DB
220 | 00DC
221 | 00DD
222 | 00DE
223 | 00DF
224 | 00E0
225 | 00E1
226 | 00E2
227 | 00E3
228 | 00E4
229 | 00E5
230 | 00E6
231 | 00E7
232 | 00E8
233 | 00E9
234 | 00EA
235 | 00EB
236 | 00EC
237 | 00ED
238 | 00EE
239 | 00EF
240 | 00F0
241 | 00F1
242 | 00F2
243 | 00F3
244 | 00F4
245 | 00F5
246 | 00F6
247 | 00F7
248 | 00F8
249 | 00F9
250 | 00FA
251 | 00FB
252 | 00FC
253 | 00FD
254 | 00FE
255 | 00FF
256 | 0100
257 | 0101
258 | 0102
259 | 0103
260 | 0104
261 | 0105
262 | 0106
263 | 0107
264 | 0108
265 | 0109
266 | 010A
267 | 010B
268 | 010C
269 | 010D
270 | 010E
271 | 010F
272 | 0110

## 工作表2
MODBUS參數
工作模式 | RTU
鮑率 | 9600bps
字元長度 | 8bit
奇偶校驗 | 無
停止位元 | 1
冗餘檢查 | CRC16-IBM (x16+x15+x2+1)(Modbus)
通訊間隔 | >5ms
通訊週期 | >300ms
MODBUS ID | 0-63 (Max 64 Device)
電器介面 | RS485 2-Wire cabling
連接器型式 | D-Sub Connector